[Code of Federal Regulations]

[Title 49, Volume 2]

From the U.S. Government Printing Office via GPO Access

[CITE: 49CFR180.209]

[Page 1051-1054]

TITLE 49--TRANSPORTATION

CHAPTER I--RESEARCH AND SPECIAL PROGRAMS ADMINISTRATION, DEPARTMENT OF

TRANSPORTATION

PART 180--CONTINUING QUALIFICATION AND MAINTENANCE OF PACKAGINGS

--Table of Contents

Subpart C--Qualification, Maintenance and Use of Cylinders

Sec. 180.209  Requirements for requalification of specification cylinders.

(a) Periodic qualification of cylinders. (1) Each specification

cylinder that becomes due for periodic requalification, as specified in

the following table, must be requalified and marked in conformance with

the requirements of this subpart. Requalification records must be

maintained in accordance with Sec. 180.215. Table 1 follows:

Table 1.--Requalification of Cylinders \1\

------------------------------------------------------------------------

Specification under which       Minimum test

cylinder was made       pressure  (psig) \2\  Test period  (years)

------------------------------------------------------------------------

DOT 3.......................  3000 psig...........  5

DOT 3A, 3AA.................  5/3 times service     5, 10, or 12 (see

pressure, except      Sec.  180.209(b),

noncorrosive          (f), (h), and (j)

service (see Sec.

180.209(g)).

DOT 3AL.....................  5/3 times service     5 or 12 (see Sec.

pressure.             180.209(j))

DOT 3AX, 3AAX...............  5/3 times service     5

pressure.

3B, 3BN.....................  2 times service       5 or 10 (see Sec.

pressure (see Sec.    180.209(f))

180.209(g)).

3E..........................  Test not required...

3HT.........................  5/3 times service     3 (see Secs.

pressure.             180.209(i) and

180.213(c))

3T..........................  5/3 times service     5

pressure.

4AA480......................  2 times service       5 or 10 (see Sec.

pressure (see Sec.    180.209(e)(14)

180.209(g)).

4B, 4BA, 4BW, 4B-240ET......  2 times service       5, 10, or 12 (see

pressure, except      Sec.  180.209(e),

non-corrosive         (f), and (j))

service (see Sec.

180.209(g)).

4D, 4DA, 4DS................  2 times service.....  5

DOT 4E......................  2 times service       5

pressure, except

non-corrosive (see

Sec.  180.209(g)).

4L..........................  Test not required...

8, 8AL......................  ....................  10 or 20 (see Sec.

180.209(i))

Special Permit cylinder..........  See current           See current

special permit.            special permit

Foreign cylinder (see Sec.    As marked on          5 (see Secs.

173.301(j) of this            cylinder, but not     180.209(KB) and

subchapter for restrictions   less than 5/3 of      180.213(d)(iii))

on use).                      any service or

working pressure

marking.

------------------------------------------------------------------------

\1\ Any cylinder not exceeding 2 inches outside diameter and less than 2

feet in length is excepted from volumetric expansion test.

\2\ For cylinders not marked with a service pressure, see Sec.

173.301(e)(1) of this subchapter.

(b) DOT 3A or 3AA cylinders. (1) A cylinder conforming to

specification DOT 3A or 3AA with a water capacity of 56.7 kg (125 lb) or

less that is removed from

[[Page 1052]]

any cluster, bank, group, rack, or vehicle each time it is filled, may

be requalified every ten years instead of every five years, provided the

cylinder conforms to all of the following conditions:

(i) The cylinder was manufactured after December 31, 1945.

(ii) The cylinder is used exclusively for air; argon; cyclopropane;

ethylene; helium; hydrogen; krypton; neon; nitrogen; nitrous oxide;

oxygen; sulfur hexafluoride; xenon; fluorinated hydrocarbons, liquefied

hydrocarbons, and mixtures thereof that are commercially free from

corroding components; permitted mixtures of these gases (see

Sec. 173.301(d) of this subchapter); and permitted mixtures of these

gases with up to 30 percent by volume of carbon dioxide, provided the

gas has a dew point at or below minus (52  deg.F) at 1 atmosphere.

(iii) Before each refill, the cylinder is removed from any cluster,

bank, group, rack or vehicle and passes the hammer test specified in CGA

Pamphlet C-6 (incorporated by reference; see Sec. 171.7 of this

subchapter).

(iv) The cylinder is dried immediately after hydrostatic testing to

remove all traces of water.

(v) The cylinder is not used for underwater breathing.

(vi) Each cylinder is stamped with a five-pointed star at least one-

fourth of an inch high immediately following the test date.

(2) If, since the last required requalification, a cylinder has not

been used exclusively for the gases specifically identified in paragraph

(b)(1)(ii) of this section, but currently conforms with all other

provisions of paragraph (b)(1) of this section, it may be requalified

every 10 years instead of every five years, provided it is first

requalified and examined as prescribed by Sec. 173.302a(b) (2), (3) and

(4) of this subchapter.

(3) Except as specified in paragraph (b)(2) of this section, if a

cylinder, marked with a star, is filled with a compressed gas other than

as specified in paragraph (b)(1)(ii) of this section, the star following

the most recent test date must be obliterated. The cylinder must be

requalified five years from the marked test date, or prior to the first

filling with a compressed gas, if the required five-year requalification

period has passed.

(c) DOT 4-series cylinders. A DOT 4-series cylinder, except a 4L

cylinder, that at any time shows evidence of a leak or of internal or

external corrosion, denting, bulging or rough usage to the extent that

it is likely to be weakened appreciably, or that has lost five percent

or more of its official tare weight must be requalified before being

refilled and offered for transportation. (Refer to CGA Pamphlet C-6 or

C-6.3, as applicable, regarding cylinder weakening.) After testing, the

actual tare weight must be recorded as the new tare weight.

(d) Cylinders 5.44 kg (12 lb) or less with service pressures of 300

psig or less. A cylinder of 5.44 (12 lb) or less water capacity

authorized for service pressure of 300 psig or less must be given a

complete external visual inspection at the time periodic requalification

becomes due. External visual inspection must be in accordance with CGA

Pamphlet C-6 or C-6.1 (incorporated by reference; see Sec. 171.7 of this

subchapter). The cylinder may be proof pressure tested. The test is

successful if the cylinder, when examined under test pressure, does not

display a defect described in Sec. 180.205(i)(1) (ii) or (iii). Upon

successful completion of the test and inspection, the cylinder must be

marked in accordance with Sec. 180.213.

(e) Proof pressure test. A cylinder made in conformance with

specifications DOT 4B, 4BA, 4BW, or 4E used exclusively for: liquefied

petroleum gas that meets the requirements in Table I of ASTM D 1835,

Standard Specification for Liquefied Petroleum (LP) Gases (incorporated

by reference; see Sec. 171.7 of this subchapter); anhydrous

dimethylamine; anhydrous methylamine; anhydrous trimethylamine; methyl

chloride; methylacetylene-propadiene stabilized; or

dichlorodifluoromethane, difluoroethane, difluorochloroethane,

chlorodifluoromethane, chlorotetrafluoroethane, trifluorochloroethylene,

or mixture thereof, or mixtures of one or more with

trichlorofluoromethane; and commercially free from corroding components

and protected externally by a suitable corrosion-resistant coating

[[Page 1053]]

(such as galvanizing or painting) may be requalified by volumetric

expansion testing every 12 years instead of every five years. As an

alternative, the cylinder may be subjected to a proof pressure test at

least two times the marked service pressure, but this latter type of

test must be repeated every seven years after expiration of the first

12-year period. When subjected to a proof pressure test, the cylinder

must be carefully examined under test pressure and removed from service

if a leak or defect is found.

(f) Poisonous materials. A cylinder conforming to specification DOT

3A, 3AA, 3B, 4BA, or 4BW having a service pressure of 300 psig or less

and used exclusively for methyl bromide, liquid; mixtures of methyl

bromide and ethylene dibromide, liquid; mixtures of methyl bromide and

chlorpicrin, liquid; mixtures of methyl bromide and petroleum solvents,

liquid; or methyl bromide and nonflammable, nonliquefied compressed gas

mixtures, liquid; commercially free of corroding components, and

protected externally by a suitable corrosion resistant coating (such as

galvanizing or painting) and internally by a suitable corrosion

resistant lining (such as galvanizing) may be tested every 10 years

instead of every five years, provided a visual internal and external

examination of the cylinder is conducted every five years in accordance

with CGA Pamphlet C-6 (incorporated by reference; see Sec. 171.7 of this

subchapter). The cylinder must be examined at each filling, and rejected

if a dent, corroded area, leak or other condition indicates possible

weakness.

(g) Visual inspections. A cylinder conforming to a specification

listed in the table in this paragraph and used exclusively in the

service indicated may, instead of a periodic hydrostatic test, be given

a complete external visual inspection at the time periodic

requalification becomes due. External visual inspection must be in

accordance with CGA Pamphlet C-6 or C-6.3, as applicable (incorporated

by reference; see Sec. 171.7 of this subchapter). When this inspection

is used instead of hydrostatic pressure testing, subsequent inspections

are required at five-year intervals after the first inspection. After

September 30, 2003, inspections must be made only by persons holding a

current RIN and the results recorded and maintained in accordance with

Sec. 180.215. Records must include: date of inspection (month and year);

DOT specification number; cylinder identification (registered symbol and

serial number, date of manufacture, and owner); type of cylinder

protective coating (including statement as to need of refinishing or

recoating); conditions checked (e.g., leakage, corrosion, gouges, dents

or digs in shell or heads, broken or damaged footring or protective ring

or fire damage); disposition of cylinder (returned to service, returned

to cylinder manufacturer for repairs or condemned). A cylinder passing

requalification by the external visual inspection must be marked in

accordance with Sec. 180.213. Specification cylinders must be in

exclusive service as shown in the following table:

------------------------------------------------------------------------

Cylinders conforming to--              Used exclusively for--

------------------------------------------------------------------------

DOT 3A, DOT 3AA, DOT 3A480X, DOT 4AA480  Anhydrous ammonia of at least

99.95% purity.

DOT 3A, DOT 3AA, DOT 3A480X, DOT 3B,     Butadiene, inhibited, that is

DOT 4B, DOT 4BA, DOT 4BW.                commercially free from

corroding components.

DOT 3A, DOT 3A480X, DOT 3AA, DOT 3B,     Cyclopropane that is

DOT 4AA480, DOT 4B, DOT 4BA, DOT 4BW.    commercially free from

corroding components.

DOT 3A, DOT 3AA, DOT 3A480X, DOT 4B,     Fluorinated hydrocarbons and

DOT 4BA, DOT 4BW, DOT 4E.                mixtures thereof that are

commercially free from

corroding components.

DOT 3A, DOT 3AA, DOT 3A480X, DOT 3B,     Liquefied hydrocarbon gas that

DOT 4B, DOT 4BA, DOT 4BW, DOT 4E.        is commercially free from

corroding components.

DOT 3A, DOT 3AA, DOT 3A480X, DOT 3B,     Liquefied petroleum gas that

DOT 4B, DOT 4BA, DOT 4BW, DOT 4E.        meets the requirements in

Table I of ASTM D 1835,

Standard Specification for

Liquefied Petroleum (LP) Gases

(incorporated by reference;

see Sec.  171.7 of this

subchapter).

DOT 3A, DOT 3AA, DOT 3B, DOT 4B, DOT     Methylacetylene-propadiene,

4BA, DOT 4BW, DOT 4E.                    stabilized, that is

commercially free from

corroding components.

DOT 3A, DOT 3AA, DOT 3B, DOT 4B, DOT     Anhydrous mono,

4BA, DOT 4BW.                            di,trimethylamines that are

commercially free from

corroding components.

DOT 4B240, DOT 4BW240..................  Ethyleneimine, inhibited.

------------------------------------------------------------------------

[[Page 1054]]

(h) Cylinders containing anhydrous ammonia. A cylinder conforming to

specification DOT 3A, 3A480X, or 4AA480 used exclusively for anhydrous

ammonia, commercially free from corroding components, and protected

externally by a suitable corrosion-resistant coating (such as paint) may

be requalified every 10 years instead of every five years.

(i) Requalification of DOT-8 series cylinders. (1) Each owner of a

DOT-8 series cylinder used to transport acetylene must have the cylinder

shell and the porous filler requalified in accordance with CGA Pamphlet

C-13 (incorporated by reference; see Sec. 171.7 of this subchapter).

Requalification must be performed in accordance with the following

schedule:

----------------------------------------------------------------------------------------------------------------

Shell (visual inspection)             Porous filler requalification

requalification            ---------------------------------------

Date of cylinder manufacture   ----------------------------------------

Initial           Subsequent            Initial           Subsequent

----------------------------------------------------------------------------------------------------------------

Before January 1, 1991..........  Before January 1,   10 years..........  Before January 1,   Not required.

2001.                                   2011.

On or after January 1, 1991.....  10 years \1\......  10 years..........  3 to 20 years \2\.  Not required.

----------------------------------------------------------------------------------------------------------------

\1\ Years from date of cylinder manufacture.

\2\ For a cylinder manufactured on or after January 1, 1991, requalification of the porous filler must be

performed no sooner than 3 years, and no later than 20 years, from the date of manufacture.

(2) Unless requalified and marked in accordance with CGA Pamphlet C-

13 (incorporated by reference; see Sec. 171.7 of this subchapter) before

October 1, 1994, an acetylene cylinder must be requalified by a person

who holds a current RIN.

(3) If a cylinder valve is replaced, a cylinder valve of the same

weight must be used or the tare weight of the cylinder must be adjusted

to compensate for valve weight differential.

(4) The person performing a visual inspection or requalification

must record the results as specified in Sec. 180.215.

(5) The person performing a visual inspection or requalification

must mark the cylinder as specified in Sec. 180.213.

(j) Cylinder used as a fire extinguisher. Only a DOT specification

cylinder used as a fire extinguisher and meeting Special Provision 18 in

Sec. 172.102(c)(1) of this subchapter may be requalified in accordance

with this paragraph (j).

(1) A DOT 4B, 4BA, 4B240ET or 4BW cylinder may be tested as follows:

(i) For a cylinder with a water capacity of 5.44 kg (12 lb) or less,

by volumetric expansion test using the water jacket method or by proof

pressure test. A requalification must be performed by the end of 12

years after the original test date and at 12-year intervals thereafter.

(ii) For a cylinder having a water capacity over 5.44 kg (12 lb)--

(A) By proof pressure test. A requalification must be performed by

the end of 12 years after the original test date and at 7-year

intervals; or

(B) By volumetric expansion test using the water jacket method. A

requalification must be performed 12 years after the original test date

and at 12-year intervals thereafter.

(2) A DOT 3A, 3AA, or 3AL cylinder must be requalified by volumetric

expansion test using the water jacket method. A requalification must be

performed 12 years after the original test date and at 12-year intervals

thereafter.

(KB) Requalification of foreign cylinders filled for export. A

cylinder manufactured outside the United States, other than as provided

in Sec. 171.12a of this subchapter, that has not been manufactured,

inspected, tested and marked in accordance with part 178 of this

subchapter may be filled with compressed gas in the United States, and

shipped solely for export if it meets the following requirements, in

addition to other requirements of this subchapter:

(1) It has been inspected, tested and marked (with only the month

and year of test) in conformance with the procedures and requirements of

this subpart or the Associate Administrator has authorized the filling

company to fill foreign cylinders under an alternative method of

qualification; and

(2) It is offered for transportation in conformance with the

requirements of Sec. 173.301(l) of this subchapter.