B339

4.12 Hydrostatic Test

4.12.1

Hydrostatic tests (volumetric expansion and proof pressure tests) shall be performed in accordance with

CGA Publication C-1, except that

(a) the pressure-measuring device shall permit reading pressure to an accuracy of 1% in the range of

80–120% of the test pressure;

(b) the expansion-measuring device shall permit reading to an accuracy of 1% or 0.1 mL, whichever is

greater; and

(c) a calibration cylinder, capable of verifying the equipment accuracy to ±1% for the material, size, and

test pressure of the containers to be tested, shall be used to verify the accuracy of the equipment at the

beginning of each day.

4.12.2

The permanent expansion, where volumetric expansion measurement is required, shall not exceed 10%

of the total expansion at test pressure, unless otherwise specified.

4.12.3

The hydrostatic test shall be conducted after any heat treatment.

4.12.4

All containers failing to pass the hydrostatic test shall be rejected. Where a sample container from a lot

fails to pass the hydrostatic test, the lot shall be rejected, unless otherwise specified.

24.2.1 General Requirements

24.2.1.1

Each cylinder, sphere, or tube shall be requalified periodically in accordance with the requirements of

Clause 24.2 and Table 24.1, except as provided in Clauses 24.2.1.6 and 24.2.1.7. Table 24.1 specifies

the basic requalification procedures and periods. It also specifies alternative requalification procedures

and periods that may be used, depending on service conditions. Alternative requalification methods and

periods are referenced to specific clauses for complete descriptions of conditions under which the

alternative procedures may be used.

24.2.1.2

Hydrostatic retests with volumetric expansion measurements and proof pressure retests, as required by

Table 24.1, shall be performed in accordance with Clause 4.12.1.

24.2.1.3

Containers subject to a hydrostatic retest with volumetric expansion measurement shall also be visually

inspected both internally, inasmuch as the size of the orifice(s) permit(s), and externally, in accordance

with CGA Publication C-6, C-6.1, C-6.2, or C-6.3. The permanent expansion shall not exceed 10% of

the total expansion, except for

(a) TC-3ALM cylinders, where it shall not exceed 6%;

(b) TC-3FCM, TC-3HWM, and TC-3HTM cylinders, where it shall not exceed 5%; and

(c) TC-4EM and CTC-4E cylinders, where it shall not exceed 12%.

24.2.1.4

Containers subject to a proof pressure retest shall also be visually inspected externally, in accordance

with CGA Publication C-6.

24.2.1.5

Containers exempt from a pressure retest under Clause 24.2.9 shall be subjected to an external visual

inspection.

24.2.1.6

Containers with a capacity of 1.0 L water or less shall be exempt from periodic requalification.

24.2.1.7

Containers with a service pressure of 2.1 MPa or less and a capacity of 4.5 L of water or less, and built to

a specification that requires periodic hydrostatic retest with a volumetric expansion measurement (see

Table 24.1), shall be exempt from the volumetric expansion measurement when retested hydrostatically,

but shall be examined while under the specified retest pressure and show no leakage or other defects.

24.2.1.8

In addition to the periodic retests, whenever there is a reason to believe that the pressure-retention

integrity of a container has been adversely affected by severe dents, corrosion, excessive heat, or other

damage, the container shall be emptied and requalified before refilling.

24.2.1.9

Reheat-treated and rebuilt containers shall be processed and requalified in accordance with the container

specification before being returned to service; compliance shall be verified by an independent inspector.

Containers repaired by welding or brazing shall be requalified before being returned to service.

Licensed to/Autorisé à Jon Davignon, Galiso, Inc., on/le 8/21/2007. Single user license only. Storage, distribution or use on network prohibited./Permis d'utilisateur simple seulement. Le stockage, la distribution ou l'utilisation sur le réseau est interdit.

© Canadian Standards Association Cylinders, Spheres, and Tubes for the Transportation of Dangerous Goods

October 2002 79

24.2.1.10

A container that does not meet the requalification requirements shall be rejected or condemned.

Rejected containers may be reheat-treated, repaired, or rebuilt only in accordance with Clause 24.

24.2.1.11

Containers, except those manufactured to TC-3ALM, CTC-3AL, TC-3FCM, TC-3HTM, CTC-3HT,

TC-3HWM, TC-4EM, CTC-4E, TC-4LM, and CTC-4L specifications, may be heat-treated if they have been

rejected for excessive permanent expansion or for exposure to excessive heat. TC- 4LM and CTC-4L

cylinders exposed to excessive heat may be returned to service without retesting if the jacket and the

vacuum remain intact. Aluminum and composite cylinders exposed to a temperature exceeding 175EC

shall be condemned.

24.2.1.12

Containers that previously contained a corrosive liquid that, through its corrosive action, could affect the

structural integrity of the container shall not be used for the transportation of any compressed gas,

unless the container is retested in accordance with the requirements of the applicable specification. A

container that contained a corrosive liquid for which decontamination methods cannot remove all

significant residue or impregnation from the container shall not be used for the transportation of any

compressed gas.

24.2.1.13

A cylinder in chlorine or sulphur dioxide service manufactured before April 20, 1915, shall be retested at

3.5 MPa.

24.2.2 Ten-Year Requalification Requirements

24.2.2.1

A TC-3AM, CTC-3A, TC-3AAM, CTC-3AA, or TC-3ASM cylinder not exceeding 57 L of water capacity

may be retested every 10 years only, provided that the cylinder complies with the following:

(a) if the cylinder is in a cluster, bank, group, or rack, it is removed from the cluster, bank, group, or

rack each time it is filled;

(b) the cylinder is used exclusively for air, argon, ethylene, helium, hydrogen, krypton, neon, nitrogen,

nitrous oxide, oxygen, xenon, and mixtures of these gases, without, or with up to 30% by volume of,

carbon dioxide. These gases or mixtures shall have a dewpoint not exceeding –54EC at 101.325 kPa

(absolute);

(c) prior to each refill, the cylinder is subjected to and passes the hammer test specified in CGA

Publication C-6;

(d) the new hydrostatic test data of the cylinder meet one of the following requirements:

(i) the elastic expansion does not exceed the REE stamped on the cylinder at the time of

manufacture;

(ii) the elastic expansion does not exceed the applicable rejection limit specified in Table 2 of CGA

Publication C-5; or

(iii) either the average wall stress or the maximum wall stress does not exceed the corresponding

wall stress limitation shown in Appendix B of CGA Publication C-5;

(e) the cylinder is stamped with a 5-pointed star following the last test or retest date;

(f) the cylinder is dried immediately following the hydrostatic retest to remove all traces of free water;

and

(g) the cylinder is not used in a self-contained respirator or in a portable resuscitator.

Note: Cylinders used in a self-contained respirator or in a portable resuscitator are to be retested, maintained, and

inspected by a registered retester in accordance with the requirements of CSA Standard CAN/CSA-Z94.4.

Licensed to/Autorisé à Jon Davignon, Galiso, Inc., on/le 8/21/2007. Single user license only. Storage, distribution or use on network prohibited./Permis d'utilisateur simple seulement. Le stockage, la distribution ou l'utilisation sur le réseau est interdit.

B339-02 © Canadian Standards Association

80 October 2002

24.2.2.2

The retest period of a cylinder previously in compliance with Items (c), (d), (f), and (g) of

Clause 24.2.2.1, but not in compliance with Item (b) of Clause 24.2.2.1, may be changed to a 10-year

retest period only after the cylinder has been retested and confined to a gas service in compliance with

Item (b) of Clause 24.2.2.1.

24.2.2.3

If, at any time, a cylinder marked with the star is used in a manner other than that specified in

Clause 24.2.2.1, the star following the most recent test or retest date shall be obliterated by peening.

Subsequent retests shall be conducted every 5 years.

B340 5.1.3

Before a container is filled, it shall be inspected to

(a) verify through its markings that

(i) for containers manufactured after 31 December 1992, the cylinder, sphere, or tube has been

manufactured in accordance with the requirements of CSA Standard B339; and

(ii) for containers manufactured before 1 January 1993, the cylinder, sphere, or tube has been

manufactured in accordance with a TC, CTC, or ICC Specification listed in Table 24.1 of CSA

Standard B339, or an equivalent BTC, CRC, ICC, or DOT Specification to the CTC Specifications listed in

Table 24.1 and in use in Canada before 1 January 1993;

(b) verify through its markings that the container is not due for requalification;

(c) verify that there is no visible damage to the container that could weaken its pressure retention

integrity. The standards of inspection for Specification containers listed in Table 24.1 of CSA

Standard B339 are CGA Publications C-6, C-6.1, C-6.2, C-6.3, and C-13;

(d) verify that its accessories and attachments are in good condition;

(e) ensure that the container, pressure-relief devices, valves, and other accessories are suitable for the

intended product and pressure; and

(f) verify that the previous service of the container does not exclude filling it with the intended Class 2

dangerous goods.

Note: The Transportation of Dangerous Goods Regulations should be consulted for limitations imposed for transportation

in Canada of US containers (ICC or DOT prefix).

5.1.4

Containers to be filled shall comply with the following:

(a) containers not in compliance with Clause 5.1.3(a) or Clause 6 shall not be filled unless a permit for

equivalent level of safety has been obtained from Transport Canada;

(b) before being filled, containers due for requalification shall be requalified in accordance with the

requirements of CSA Standard B339. Containers that do not meet the requirements of the prefill

inspection shall be rejected and not filled until the cause for rejection has been corrected.

1. CAN /CSA (Canadian Standards Association) stipulates that Hydrostatic Tests (both volumetric and proof pressure) be performed in accordance with CGA Publication C-1, with certain specific exceptions / conditions.

True B339 4.12.1

2.  B339 stipulates that a calibration cylinder, capable of verifying the equipment accuracy to ± 1% for the material, size, and test pressure of the materials to be tested shall be used to verify the accuracy of the equipment:

A.  Once every six months

B.  At the beginning of each day  B339 4.12.1(c)

C.  Once a month

D.  It is not necessary to use a calibration cylinder

3.  B339 stipulates that the expansion-measuring device shall permit reading to an accuracy 1% or 0.1 mL, whichever is greater.

True B339 4.12.1 (b)

4.  B339 stipulates that in the range of 80-120% of the test pressure, the pressure-measuring device shall permit reading pressure to an accuracy of:

A.  0.5%

B.  5%

C.  1%  B339 4.12.1 (a)

D.  None of the above

5.  There is no safety permit available from Transport Canada to fill containers not in compliance with Clause 5.1.3(a) or Clause 6 of B340.

False B340 5.1.4(a)

6.  B339 stipulates that containers subject to a hydrostatic retest shall also be visually inspected both internally and externally in accordance with CGA publications:

A.  C-6

B.  C-6.1

C.  C-6.2

D.  C-6.3

E.  All of the above B339 24.2.1.3

7.  Permanent expansion for TC-3ALM cylinders shall not exceed:

A.  10%

B.  6%  B339 24.2.1.3 (a)

C.  5%

D.  12%

8.  Permanent expansion for TC-3FCM, TC-3HWM and TC-3HTM cylinders shall not exceed:

A.  10%

B.  6%

C.  5% B339 24.2.1.3 (a)

D.  12%

9.  Permanent expansion for TC-4EM and CTC-4E cylinders shall not exceed:

A.  10%

B.  6%

C.  5%

D.  12% B339 24.2.1.3 (a)

10.  According to B339, containers subject to a proof pressure retest shall also be visually inspected externally, in accordance with CGA Publication C-6. True B339 24.2.1.4

11.  Containers with a capacity of 1.0 Liter of water or less are exempt from periodic requalification.  True  B339 24.2.1.6

12.  In addition to periodic retests, whenever there is reason to believe that the pressure-retention integrity of a container has been adversely affected by severe dents, corrosion, excessive heat or other damage, the container shall be emptied and requalified before refilling.  True B339 24.2.1.8

13.  If, at any time, a cylinder marked with a star is used in a manner other than that specified in Clause 24.2.2.1 of B339, the star following the most recent test or retest date shall be obliterated by peening.  True B339 24.2.2.3

14.  A TC-3AM, CTC-3A, TC-3AA, CTC-3AA, or TC-3ASM cylinder not exceeding 57 Liters of water capacity may be retested every 10 years only, provided that certain specific conditions are met as set forth in B339.

True B339 24.2.2.1

15.  Containers with a service pressure of 2.1 MPa or less and a capacity of 4.5 L of water or less shall be exempt from the volumetric expansion measurement when retested hydrostatically, but shall be examined and pass a Proof Pressure Test.  True  B339 24.2.1.7

16.  Cylinders with a service pressure of 2.1 MPa or less, in nonflammable, noncorrosive service may be retested at 10 years with a visual inspection at 5 years.  True B339 24.2.3

24.2.3 Cylinders with a Service Pressure of 2.1 MPa or Less in

Nonflammable Liquid or Mixtures of Nonflammable Liquids and

Nonflammable, Nonliquefied Compressed Gases in Noncorrosive

Service

A TC-3AM, CTC-3A, TC-3AAM, CTC-3AA, TC-3ANM, TC-3ASM, CTC-3B, or CTC-3BN cylinder used

exclusively for nonflammable liquids or mixtures of nonflammable liquids and nonflammable,

nonliquefied compressed gases in noncorrosive service may be retested every 10 years. The cylinder

shall have a service pressure of 2.1 MPa or less and, except for TC-3ASM cylinders, be protected

externally by a suitable corrosion-resistant coating, such as, but not limited to, paint, and internally by an

equally corrosion-resistant lining. Each test shall be supplemented by a visual internal and external

inspection, in accordance with CGA Publication C-6, at least once every 5 years.

17.  Cylinders used for fire extinguishers may be retested hydrostatically by water jacket every 12 years or every 7 years by proof pressure testing.  True B339 24.2.4

24.2.4 Containers Used for Fire Extinguishers

A TC-4BM, CTC-4B, TC-4BAM, CTC-4BA, TC-4BWM, CTC-4BW, TC-4BM17ET, CTC-4B240ET,

CTC-4B24OFLW, TC-4EM, or CTC-4E container used for noncorrosive liquefied or nonliquefied

compressed gases or mixtures of same and any noncorrosive fire-extinguishing agent may be

hydrostatically retested with volumetric expansion measurement every 12 years. The container shall be

protected externally by a suitable corrosion-resistant coating, such as, but not limited to, paint.

Alternatively, the same containers may be proof pressure retested every 7 years.

18.  Containers used for fire extinguishers shall be protected by corrosion-resistant coating, such as paint.  True B339 24.2.4

19.  Nonmanufacturers must receive a certificate of registration before requalifying, repairing or rebuilding used cylinders.  True B339 25.3.2

Δ 24.7.1 Requalification

Each requalification shall be recorded on a report form by the person performing the requalification.

Typical report forms are shown in

(a) Appendix E of CGA Publication C-1, for a requalification hydrostatic test;

(b) Appendix A of CGA Publication C-6, for a requalification by visual inspection only; and

(c) Appendix B of CGA Publication C-13, for requalification of series-8 cylinders.

The format of the requalification report forms may be modified, but as a minimum all information

shown on the form for the applicable test method shall be incorporated or attached. The reports shall

include a record of the required test system accuracy verification.

20.  The letter “K” is a marking used to specify the elastic expansion exceeds the REE in certain specified cylinders.  True B339 24.6.3.4

24.6.3.4

In addition to the marks required under Item (a) or (c) of Clause 24.6.3.2, a TC-3AM, TC-3AAM,

TC-3AXM, TC-3AAXM, TC-3ASM, or TC-3TM container for which the elastic expansion exceeds the REE

stamped on the cylinder at the time of manufacture or the applicable rejection limit specified in Table 2

of CGA Publication C-5, or for which the average or maximum wall stress exceeds the corresponding

limitation in Appendix B of CGA Publication C-5, shall be marked with the letter “K”, immediately

following the service pressure marking.

21.  When specific conditions are met, a metal plate may be used for remarking cylinders.

True B339 24.6.4.1-3

24.6.4 Marking Maintenance

Δ 24.6.4.1

Except as provided in Clause 24.6.4.4, any marking becoming illegible shall be remarked on the

container or reproduced on a metal plate permanently secured to the cylinder or any permanent part of

the container, excluding the sidewall.

24.6.4.2

Where attached to a nonpressure part of the container, the metal plate shall be attached by a permanent

method such as, but not limited to, riveting, welding, spot welding, or brazing.

24.6.4.3

Where the metal plate is attached to a pressure-retaining part of a container, it shall be welded or

brazed, as permitted in the applicable specification. The container shall be considered as a repaired or

rebuilt container and further processed accordingly.

22.   Requalification dates  may not be removed.

False B339 24.6.4.4

23.  The original manufacturing test date may be removed by peening.  True B339 24.6.4.4

24.6.4.4

Where the space originally provided for marking requalification dates becomes filled, the expired

requalification dates, except the last one, may be removed by peening, provided that

(a) permission to do so has been obtained from the owner of the container;

(b) the design minimum wall thickness is maintained; and

(c) the original manufacturing test date is not removed.

24.  Canadian Standards Association B339 sets forth specific marking information after requalification.  True 24.6.3.2

24.6.3.2

The marking information after requalification shall be as follows:

A B C D E

(a) for a 3- or 5-year hydrostatic retest with volumetric expansion 08 XY 94

(b) for a 7-year proof pressure retest 08 XY 94 )

(c) for a 10-year hydrostatic retest with volumetric expansion 08 XY 94 Ú

(d) for a 10-year proof pressure retest 08 XY 94 Ë

(e) for a 12-year hydrostatic retest with volumetric expansion 08 XY 94 ~

measurement

(f) for a visual reinspection 08 XY 94 E

(g) for requalification after a repair procedure 08 XY 94 R WZ

(h) for requalification after a rebuilding procedure 08 XY 94 RB WZ

(i) for requalification after reheat treatment only 08 XY 94 RH WZ

(j) for series-8 cylinder shell reinspection only 08 XY 94 S

(k) for series-8 cylinder shell and porous filler reinspection 08 XY 94 FS

25.  Typical report forms for requalification of cylinders are shown in:

A.  CGA Publication C-1

B.  CGA Publication C-6

C.  CGA Publication C-13

D.  All of the above

“Click here for Registration and Renewal Links”

25.3.2 Nonmanufacturers: Initial Registration

A certificate of registration shall be obtained from the Director prior to requalifying, repairing, reheat

treating, or rebuilding used containers.

25.3.3.2

Application for the renewal of a certificate of registration is required no later than 5 years from the date

of issue of the previous certificate. An application for renewal of a certificate of registration shall include

information required in Clause 25.3.2.

Note: Only changes to the information provided in the original application pursuant to Clause 25.3.2 are required. If

no changes have occurred, a statement to that effect should be made in the application for renewal.

25.3.3.3

A certificate of registration shall remain valid beyond 5 years if, following a bona fide application for

renewal of registration by registered mail, made prior to the expiry date, a new certificate is not issued

and the certificate due to expire is not revoked by the Director.